## IMC
IMC Existing Amendment Review
Summary: |  | Repeal existing state amendment |  | Keep existing amendment as modified |  |  | Keep existing amendment
Last Updated 3/15/2021 | [6 empty] | May include renumbering
| WAC | Title or Subject | 2018 IMC Number | Existing Amendment Subject | 2021 IMC Number | Staff Recommendation | TAG Recommendation | Comments
01 Scope and Administration
TAG Member:
| 51-52-0101 | General - Adds reference to NFPA 54 and 58 as required by statute for LP gas installations | 101.2 | Scope | 101.2 | Update to latest editions of NFPA 54 (2021), NFPA 58 (2020)
02 Definitions
TAG Member:
51-50-0202
|  | Balanced whole house ventilation |  | 2021 IMC adds a new definition for Balanced ventilation that is similar but missing the second sentence |  | Remove state amendment. Second sentence is a code exception that should be moved to Chapter 4.
Balanced whole house ventilation. Any combination of concurrently operating residential unit mechanical exhaust and mechanical supply whereby the total mechanical exhaust airflow rate is within 10 percent or 5 cfm, whichever is greater, of the total mechanical supply airflow rate. Intermittent dryer exhaust, intermittent range hood exhaust, and intermittent toilet room exhaust airflow rates above the residential dwelling or sleeping unit minimum ventilation rate are exempt from the balanced airflow calculation. [2021 IMC] BALANCED VENTILATION. Any combination of concurrently operating mechanical exhaust and mechanical supply whereby the total mechanical exhaust airflow rate is within 10 percent of the total mechanical supply airflow rate.
|  | Distributed whole house ventilation |  | WA only language |  | Retain state amendment
|  | Local exhaust |  | WA only language |  | Retain state amendment
|  | Permanent construction |  | WA only language |  | Retain state amendment
|  | Relief air |  | WA only language |  | Retain state amendment
|  | Replacement air |  | WA only language |  | Retain state amendment
|  | Whole house ventilation system |  | WA only language |  | Retain state amendment
|  | Ventilation zone |  | WA only language |  | Retain state amendment
03 General Regulations
TAG Member:
51-52-0306
|  | Equipment and appliances on roofs or elevated structures | 306.5 | Modifies heights to match WISHA standards | 306.5 | Retain state amendment
|  | Appliances above ceilings | 306.6 | WA only language | 306.6 | Retain state amendment
51-52-0307
|  | Auxiliary and secondary drain systems | 307.2.3 | Added exception to the requirement for water-level dectection devices for unducted fain coil units | 307.2.3 | Retain state amendment
|  | Ductless mini-split system traps | 307.2.4.1 | Adds allowance for other means of condensate drainage | 307.2.4.1 | Retain state amendment
04 Ventilation
TAG Member:
51-52-0401
|  | Ventilation required | 401.2 | Reformats section into subsections that point to state requirements | 401.2 | Retain state amendment
|  | Group R occupancies | 401.2.1 | WA language pointer for whole house ventilation requirements | 401.2.1 | Retain state amendment
|  | Ambulatory care facilities and Group I-2 occupancies | 401.2.2 | WA amendment pulled from 401.2 | 401.2.2 | Retain state amendment
|  | All other occupancies | 401.2.3 | WA amendment pulled from 401.2 | 401.2.3 | Retain state amendment
|  | When required | 401.3 | Specific charging language for whole house ventilation is added | 401.3 | Retain state amendment
|  | Intake opening location | 401.4 | Two exceptions are added regarding environmental air exahust and intake openings and enclosed parking garage intake openings. 2021 IMC adds language to item 3 that is effectively the same as the first state added exception. | 401.4 | Modify the state amendment to delete the exception to item 3 and replace it with the new 2021 IMC language
3. Intake openings shall be located not less than 3 feet (914 mm) below contaminant sources where such sources are located within 10 feet (3048 mm) of the opening. Separation is not required between intake air openings and living space exhaust air openings of an individual dwelling unit or sleeping unit where an approved factory-build intake/exhaust combination termination fitting is used to separate the air streams in accordance with the manguacturer’s instruction. Exception: Separation is not required between intake air openings and living space environmental air exhaust air openings of an individual dwelling unit or sleeping unit where a factory-built intake/exhaust combination termination fitting is used to separate the air streams in accordance with the manufacturer's instructions. A minimum of 3 feet (914 mm) separation shall be maintained between other environmental air exhaust outlets and other dwelling or sleeping unit factory-built intake/exhaust combination termination fittings.
|  | Testing and balancing | 401.7 | WA only language allowing the code official to require flow testing | 401.7 | Modify the state amendment to replace "building official" with "code official"
51-52-0403
|  | Ventilation system | 403.1 | Removes reference to Group R requirements | 403.1 | Retain state amendment
|  | Outdoor air required | 403.2 | Adds an allowance for using ASHRAE 62.2 | 403.2 | Retain state amendment
|  | Recirculation of air | 403.2.1 | Deletes the allowance for reciruclation of air within footnote b spaces; adds an allowance for recirculating footnote g spaces when returned to an ERV | 403.2.1 | Modify the state amendment with the 2021 IMC language for item 2
|  | Outdoor air and local exhaust airflow rates | 403.3 | Pointer to whole house ventilation requirements in lieu of IMC requirements | 403.3 | Retain state amendment
|  | Outdoor airflow rate | 403.3.1.1 | Adds requirements for outdoor air to be ducted to each occupiable space; exception clarified with a backstop | 403.3.1.1 | Retain state amendment
|  | Minimum ventilation rates | Table 403.3.1.1 | Adds categories for kitchenettes, elevator lobbies, ice areas, janitor closets; refrigerated spaces moved to workrooms; Group R references whole house section | Table 403.3.1.1 | Retain state amendment
|  | Multiple zone recirculating systems | 403.3.1.1.2.3 (and all subsections | Replaces all the multiple-space language and equations with the requirements from ASHRAE 62.1 | Same | Retain state amendment
|  | Group R-2, R-3 and R-4 occupancies | 403.3.2 (and all subsections) | Pointer to whole house ventilation requirements in lieu of IMC requirements | Same | Retain state amendment
|  | Whole house ventilation | 403.4 (and all subsections) | State whole house ventilation requirements | Same | Retain state amendment
| 51-52-0404 | Automobile repair facilities | 404.3 | Requires exhaust extension ducts to be furnished at each repair bay and all offices and waiting rooms to be under positive pressure | 404.3 | Retain state amendment
| 51-52-0407 | General (ambulatory care facilities) | 407.1 | Pointer to the DOH requirements | 407.1 | Retain state amendment
05 Exhaust Systems
TAG Member:
| 51-52-0501 | Location of exhaust outlet | 501.3.1 | Adds specific requirements for enclosed parking garages and transformer vaults; also adds three exceptions to environmental air exhaust requirements | 501.3.1 | Modify the state amendment with the 2021 IMC language for item 3 allowing combination termination fittings
|  | Pressure equalization | 501.4 | Adds an exception for residential range, dryer and local exhaust | 501.4 | Retain state amendment
| 51-52-0504 | Exhaust installation | 504.4 | Allows wall louvers with at least 1/2-inch spacing; prohibits dryer ducts from penetrating other ducts or plenums; allows ducts to terminate at a common location with individual back draft dampers | 504.4 | Retain state amendment
|  | Common exhaust systems for clothes dryers in multistory structures | 504.1 | Item 9 is amended for clarity | 504.11 | Retain state amendment but renumber
| 51-52-0505 | Exhaust ducts | 505.3 | Original proposal was to allow ducts to terminate at a common exhaust when equipped individually with backdraft dampers | 505.3 | Revise to update with new language introduced in 2015 while keeping the last two sentences of the state amendment
505.3 Exhaust ducts. Domestic ooking exhaust equipment Where domestic range hoods and domestic appliances
equipped with downdraft exhaust are provided, such hoods and appliances shall discharge to the outdoors through
sheet metal ducts constructed of galvanized steel, stainless steel, aluminum or copper. Such ducts shall have smooth
inner walls, shall be air tight, shall be equipped with a backdraft damper and shall be independent of all other exhaust
systems. Installations in Group I-1 and I-2 occupancies shall be in accordance with the International Building Code and
Section 904.13 of the International Fire Code.
Domestic kitchen exhaust ducts may terminate with other domestic dryer exhaust and residential local exhaust ducts
at a common location where each duct has an independent back-draft damper.
Listed and labeled exhaust booster fans shall be permitted when installed in accordance with the manufacturer's
installation instructions.
Exceptions:
In other than Group I-1 and I-2, where installed in accordance with the manufacturer's installation instructions
and where mechanical or natural ventilation is otherwise provided in accordance with
| 51-52-0506 | Vibration isolation | 506.3.2.4 | Allows an option for fan flexible connectors per Section 506.3.2.3 | 506.3.2.4 | Retain state amendment
|  | Grease duct cleanout location, spacing and installation | 506.3.9 (and subsections) | Adds requirements for vertical cleanouts | Same | Add new 2021 IMC item 7 to existing state amendment in 506.3.9.1 (7. Be located within 3 feet of horizontal discharge fans.)
|  | Grease duct enclosures | 506.3.11 | Sets the maximum at 2 hr fire resistance rating | 506.3.11 | Retain state amendment
| 51-52-0507 | Domestic Cooking appliances used for commercial purposes | 507.1.2 | Adds a table specifying when a residential hood is allowed--same amendment is in the fire code | 507.1.2 | Retain state amendment
|  | Type I hoods | 507.2 | Adds an exception for R-2 with less than 16 residents | 507.2 | Retain state amendment
| 51-25-0515 | Waste or linen chute venting | 515 | Allows chutes to be vented in accordance to either NFPA 82 or the IBC | 515 | Retain state amendment (but fix the language from "per" to "in accordance with")
06 Duct Systems
TAG Member:
| 51-52-0601 | Air movement in egress elements | 601.2 | Adds exceptions for engineered smoke control systems and residential occupancies | 601.2 | Revise exception 4 to match new IMC/IBC language
| 51-52-0602 | General (Plenums) | 602.1 | Clarifying that air systems must be ducted from the air handler to the area served if the system serves multiple fire areas. | 602.1 | Retain state amendment (NOTE: there was an additional sentence added in the 2018 code referencing 602.3 for framing cavities used as plenums that was not adopted)
| 51-52-0603 | Gypsum ducts | 603.5.1 | Exception added to allow gypsum ducts in other than I-2 for stair or elevator pressurization only | 603.5.1 | Retain exising exception but add the editorial changes from the 2021 IMC
| 51-52-0605 | General (Air filters) | 605.1 | Adds exception to not require filters upstream for cooling coils | 605.1 | Retain the state amendment
|  | Particulate matter removal | 605.4 | Requires MERV 6 filters for air handlers | 605.4 | Retain the state amendment
| 51-52-0606 | Return air systems | 606.2.1 | Adds exception to not require smoke detectors for makeup air systems or where all air is exhausted | 606.2.1 | Retain the state amendment
|  | Common supply and return air systems | 606.2.2 | Adds requirements for the control system used to shut down fan powered terminal units | 606.2.2 | Retain the state amendment
|  | Corridors serving Group R/not highrise and highrise | 606.2.4/606.2.5 | Adds sections on residential corridor smoke detection requirements | 606.2.4/606.2.5 | Retain the state amendment
07 Combustion Air
TAG Member:
- None -
08 Chimneys and Vents
TAG Member:
- None -
09 Specific Appliances, Fireplaces and Solid Fuel-Burning Equipment
TAG Member:
- None -
10 Boilers, Water Heaters and Pressure Vessels
TAG Member:
| 51-52-1000 | Informational Note | 1000 | Adds pointer to L&I boiler requirements | same | Retain state amendment
| 51-52-1000 | Scope | 1001.1 | Helps clarify that boilers are under L&I rules | 1001.1 | Retain state amendment
11 Refrigeration
TAG Member:
| 51-52-1101 | General (Refrigeration) | 1101.2/1101.6 | Adding references for LGW refrigerant standards | Same | Delete state amendment; covered by model code |  | Note: There is an expedited rule in progress for this section
| 51-52-1105 | Ventilation rate | 1105.6.3 | Adds a missing phrase to the ammonia ventilation requirements | 1105.6.3 | Delete state amendment - sentence removed from model code
| 51-52-1106 | Emergency ventilation system | 1106.5.2 | Corrects a reference in the table--from R143 to R143a | 1106.4.3 | Retain state amendment but renumber
12 Hydronic Piping
TAG Member:
| 51-52-1200 | Thermal barrier required | 1209.5 |  | 1209.5 | Retain state amendment (as fixed in the expedited rule) |  | Note: There is an expedited rule in progress for this section
WAC 51-52-1200 Chapter 12—Hydronic piping. 1209.5 Thermal barrier required. Radiant floor heating and snow melt systems shall be provided with a thermal barrier in accordance with Sections 1209.5.1 and 1209.5.2. Concrete slab-on-grade, asphalt and paver-system type pavements shall have a minimum of R-10 insulation installed under the area to be snow melted, or R-5 insulation shall be installed under and at the slab edges of the area to be snow melted. The insulation shall be located underneath the snow and ice melt hydronic piping or cable and along all edges of the pavement where the snow and ice melt system is installed in accordance with the snow and ice melt manufacturer's instructions. Insulation R-values for slab-on-grade and suspended floor insulation shall be in accordance with the Washington State Energy Code.
| 51-52-1200 | Slab-on-grade installation | 1209.5.1 | (Deleted in expedited rule--text is now in 1209.5) | 1209.5.1 | (Deleted in expedited rule)
| 51-52-1200 | Expansion tanks | 1210.7.6 | Adds requirement for draining the expansion tank | 1210.7.6 | Retain state amendment
13 Fuel Oil Piping and Storage
TAG Member:
- None -
14 Solar Thermal Systems
TAG Member:
| 51-52-1400 | Rooftop-mounted solar thermal collectors and systems | 1402.8.1.2 | Replaced supporting construction with mounting systems & attachments | 1402.8.1.2 | Delete state amendment--covered in model code
15 Referenced Standards
TAG Member:
| 51-52-1500 | Referenced Standards
|  | ANCE 60335-2-40-2019 |  |  |  | Retain state amendment (although it is listed under UL without the ANCE reference, but as the 2017 edition)
|  | ASHRAE 15-2019 |  |  |  | Delete state amendment
|  | ASHRAE 34-2019 |  |  |  | Delete state amendment
|  | ASHRAE 62.2-2016 |  |  |  | Retain state amendment but update to 2019 edition
|  | CSA 60335-2-40-2019 |  |  |  | Retain state amendment (although it is listed under UL a without the ANCE reference, but as the 2017 edition)
|  | HVI 915/916/920-2015 |  |  |  | Retain state amendment but update to 2020 edition
|  | UL 864-03 |  |  |  | Retain state amendment but update to 2014/October 2018 edition and just add the reference to Section 606.2.2
|  | UL/CSA/ANCE 60335-2-40-2019 |  |  |  | Retain state amendment (although it is listed under UL a without the ANCE reference, but as the 2017 edition)

## IRC Mechanical
IRC Mechanical Existing Amendment Review
Summary: |  | Repeal existing state amendment |  | Keep existing amendment as modified |  |  | Keep existing amendment
May include renumbering
| WAC | Title or Subject | 2018 IRC Number | Title or Subject | 2021 IRC Number | TAG Member Recommendation | TAG Recommendation | Comments
Chapter 12 Mechanical Administration
TAG Member Assigned:
| 51-51-1201 | Scope | M1201.1 | General - Adds reference to NFPA 54 and 58 as required by statute for LP gas installations | M1201.1 | Update to latest editions of NFPA 54 (2021), NFPA 58 (2020)
| 51-51-1201 | Construction documents | M1201.3 | WA only language--Requires system information on plans | M1201.3 | Retain state amendment
| 51-51-1201 | Testing | M1201.4 | WA only language--Allows building official to require flow testing | M1201.4 | Retain state amendment
Chapter 13 General Mechanical Requirements
TAG Member Assigned:
| 51-51-1301 | Identification | M1301.2 | Adds an exception for identification for small fittings to be printed on packaging | M1301.2 | Retain state amendment
| 51-51-1307 | Anchorage of appliances | M1307.2 | Requires seismic strapping in accordance with the plumbing code | C1307.2 | Retain state amendment
Chapter 14 Heating and Cooling Equipment and Appliances
TAG Member Assigned:
| 51-51-1413 | General | M1413.1 | Changes reference from IPC to state plumbing code | M1413.1 | Retain state amendment (but fix typo and update section reference)
Chapter 15 Exhaust Systems
TAG Member Assigned:
| 51-51-1503 | Open-top broiler exhaust | M1503.2.1 | Adds an exception allowing outdoor broiler units without hoods | M1503.2.1 | Retain state amendment
| 51-51-1504 | Exhaust openings | M1504.3 | Adds an allowance for H/ERV installed per MII | M1504.3 | Retain state amendment
| 51-51-1505 | Mechanical ventilation | M1505.4 (and all subsections) | State whole house ventilation requirements | Same | Retain state amendment
Chapter 16 Duct Systems
TAG Member Assigned:
| 51-51-1600 | Above-ground duct systems | M1601.1.1 | State amendment is Item 7, not allowing wall cavities and floor spaces to be used as plenum | M1601.1.1 | Retain state amendment but modify to include new item 7.6, Item 8 (from 2018) and the new sentence at the send of 7.4.
Chapter 17 Combustion Air
TAG Member Assigned:
| 51-51-1700 | Scope | M1701.1 | Adds a pointer to Chapter 10 for fireplaces | M1701.1 | Retain state amendment
Chapter 20 Boilers and Water Heaters
TAG Member Assigned:
| 51-51-2000 | Informational Note | M2000 | Adds pointer to L&I boiler requirements | same | Retain state amendment
| 51-51-2000 | General | M2005.1 | Changes reference from IPC to state plumbing code | M2005.1 | Retain state amendment
Chapter 21 Hydronic Piping
TAG Member Assigned:
| 51-51-2101 | Protection of potable water | M2101.3 | Changes reference from IPC to state plumbing code | M2101.3 | Retain state amendment
| 51-51-2101 | Prohibited tee applications | M2101.7 | Section removed to allow secondary pumping | M2101.7 | Retain state amendment
| 51-51-2103 | Piping joints | M2103.3 | Changes reference from IPC to state plumbing code | M2103.3 | Retain state amendment
| 51-51-2105 | CPVC plastic pipe | M2105.9 | Changes reference from IPC to state plumbing code | M2105.9 | Retain state amendment
| 51-51-2105 | PVC plastic pipe | M2105.14 | Changes reference from IPC to state plumbing code | M2105.14 | Retain state amendment
| 51-51-2105 | Protection of potable water | M2105.18 | Changes reference from IPC to state plumbing code | M2105.18 | Retain state amendment
| 51-51-2105 | Pipe penetrations | M2105.19 | Changes reference from IPC to state plumbing code | M2105.19 | Retain state amendment
Chapter 23 Solar Thermal Energy Systems
TAG Member Assigned:
| 51-51-2300 | Solar Thermal Energy Systems | M2300 etc | Changes references from IRC plumbing and IRC energy changes to Washington state references | Same | Retain state amendments
Chapter 24 Fuel Gas
TAG Member Assigned:

## IFGC
IFGC Existing Amendment Review
Summary: |  | Repeal existing state amendment |  | Keep existing amendment as modified |  |  | Keep existing amendment
May include renumbering
| WAC | Title or Subject | 2018 IFGC Number | Title or Subject | 2021 IFGC Number | TAG Member Recommendation | TAG Recommendation | Comments
TAG Member:
| 51-52-21101 | General - Adds reference to NFPA 54 and 58 as required by statute for LP gas installations | 101.2 | Scope | 101.2 | Update to latest editions of NFPA 54 (2021), NFPA 58 (2020)