PLEASE FOLLOW INSTRUCTIONS ON PAGE FIVE

**1. State Building Code to be Amended:**

 [X] International Building Code [ ] State Energy Code

 [ ] International Existing Building Code [ ] International Mechanical Code

 [ ] ICC ANSI A117.1 Accessibility Code [ ] International Fuel Gas Code

 [ ] International Residential Code [ ] NFPA 54 National Fuel Gas Code

 [ ] International Fire Code [ ] NFPA 58 Liquefied Petroleum Gas Code

 [ ] Uniform Plumbing Code

 **Section** Sections 202 and 504.3  **Pages**: 11 & 96

**2. Applicant Name (Specific local government, organization or individual):**

 Lee J. Kranz, representing the WABO Technical Code Development Committee

**3. Signed:**

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Plan Review Supervisor \_\_\_\_1-29-14

 **Proponent Title Date**

**4. Designated Contact Person:**

Lee J. Kranz Building Code Plan Review Supervisor, City of Bellevue

 **Name Title**

 **Address:** 450 110th Ave. NE

 Bellevue, WA. 98004

 \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

 Office **Phone:** (425) 452-2732\_\_\_\_\_\_\_\_ **Cell:**(206) 915-5835

 **E-Mail address: lkranz@bellevuewa.gov**

**5. Proposed Code Amendment**. Reproduce the section to be amended. Underline all added language, strike through all deleted language. Insert any separate new sections in the appropriate place in the code in order to continue the established numbering system of the code. If more than one section is proposed for amendment or more than one page is needed for reproducing the affected section of the code, additional pages may be attached. (Please indicate number of additional pages below)

 **Codes:** 2015 IBC (with references to the 2014 NEC) **Section**s 202 & 504.3 **Page**s 11 & 96

 Amend section to read as follows:

IBC Chapter 2 Definitions

POWER SYSTEM, EMERGENCY. (Reference: NEC ARTICLE 700, Section 700.2)

Emergency Power Systems are those systems legally required and classed as emergency by municipal, state, federal, or other codes, or by any governmental agency having jurisdiction. These systems are intended to automatically supply illumination, power, or both, to designated areas and equipment in the event of failure of the normal supply or in the event of accident to elements of a system intended to supply, distribute, and control power and illumination essential for safety to human life.

POWER SYSTEM, LEGALLY REQUIRED STANDBY. (Reference: NEC ARTICLE 701Section701.2)

Legally Required Standby Power Systems are those systems required and so classed as legally required standby by municipal, state, federal, or other codes or by any governmental agency having jurisdiction. These systems are intended to automatically supply power to selected loads (other than those classed as emergency systems) in the event of failure of the normal source.

**WSBC Section 504.3**

**504.3 Stair enclosure pressurization increase.**

For Group R-1 and R-2 occupancies in buildings of Type VA construction equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, the maximum number of stories permitted in Section 504.2 ~~M~~ may be increased by one provided the interior exit stairways and ramps are pressurized in accordance with Section 909.~~20 and Section 909.11.~~

Legally required standby power shall be provided for buildings constructed in compliance with this section and be connected to stairway shaft pressurization equipment, elevators and lifts used for accessible means of egress, hoist way pressurization equipment (if provided) and other equipment as determined by the authority having jurisdiction. Legally required standby power shall comply with NEC Section 701.12, options (A), (B), (C), (D), (F) or (G).

Are additional pages attached? Yes No

Please note number of additional pages:

**Supporting Data for Statewide Amendment Proposals** This information is required for all statewide amendment proposals. **Attach supporting documentation, as necessary; incomplete proposals will not be accepted.**

**The SBCC requires supporting data on any amendment proposal to show:**

1. **That it meets basic criteria – See Part I to specify how this proposal meets the criteria for code amendment.**
2. **The intended effect—See Part II to describe the purpose of the proposed amendment, including the benefits and the problems addressed.**
3. **The potential impacts or benefits on business—See Part III/Types of Construction, to explain how methods in construction businesses, industries and services would be affected.**
4. **The potential impact on enforcement procedures, See Part III/Types of Services Required, to provide some analysis of the impacts on code enforcement in local jurisdictions.**
5. **Economic costs and benefits – Use the Table in Part IV of this form to estimate the costs and benefits of the proposal on the construction industry, the user and/or public, the enforcement community, and operation and maintenance.**

**Part I Background information on amendment.**

Code References: Title:

Related codes:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ (Does this amendment change other related codes?)

Proponent: Phone: Date:

**NOTE:** State-wide and emergency state-wide amendments to the state building code must be based on one of the following criteria; please indicate the pertinent rationale for the proposed amendment by selecting from the list below:

(1) The amendment is needed to address a critical life/safety need.

(2) The amendment is needed to address a specific state policy or statute.

(3) The amendment is needed for consistency with state or federal regulations.

(4) The amendment is needed to address a unique character of the state.

(5) The amendment corrects errors and omissions.

**Part II Amendment Benefit:**

PROBLEM(S) ADDRESSED (Describe the intended effect of the proposed code amendment): \_\_\_\_\_

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_If approved, this code change will create consistency in the State of Washington for how legally required standby power is provided for primary life safety systems in wood framed type V-A buildings that require pressurized stairways or hoist ways, emergency egress elevators, electric fire pumps and similar systems critical to preservation of life and property in the event of a fire or other catastrophic event. Definitions for Legally required standby power and Emergency power system are consistent with the National Electrical Code and provide clarity for these systems. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

PRIMARY REASON FOR AMENDMENT: (Describe how the amendment meets one of the criteria listed above) \_\_\_\_\_\_\_

This amendment is needed to address a specific state statute and to create consistency with State regulations. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

TYPE OF BENEFITS PROJECTED: More affordable housing units will be created and a reasonable level of safety for the building occupants will be provided. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**Part III Amendment Impacts or Benefits:**

TYPES OF CONSTRUCTION: 🖏 New Construction Alteration/Tenant Improvement/Repair

 Residential-Single Family 👍Residential-Multi Family Commercial Industrial

List businesses/industries affected by amendment

Fire Protection Industry: \_\_\_\_\_\_\_\_Yes\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Specific Construction Contractors & Trades: \_\_\_\_\_\_\_\_Electrical, mechanical fire protection system designers \_\_\_\_\_\_\_\_\_

Construction Supply Industry: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Specialty Trades: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Types of Buildings: \_\_\_\_Type V-A wood framed one-hour rated \_\_\_\_\_\_\_\_\_\_\_

Manufacturers: \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

Types of Services Required:

List any reporting, record keeping or other requirements. Indicate if equipment, material or services required by this proposal are available from multiple sources. \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**Part IV Amendment Costs and Benefits**

|  |  |  |  |
| --- | --- | --- | --- |
| Building Type |  Construction[[1]](#footnote-1) |  Enforcement[[2]](#footnote-2) | Operations & Maintenance[[3]](#footnote-3) |
| Costs | % impact4 | Benefits5 | Costs | % impact[[4]](#footnote-4) | Benefits[[5]](#footnote-5) | Costs | % impact4 | Benefits5 |
| Residential |  |  |  |  |  |  |  |  |  |
|  Single family |  |  |  |  |  |  |  |  |  |
|  Multi-family |  |  |  |  |  |  |  |  |  |
| Commercial/Retail |  |  |  |  |  |  |  |  |  |
| Industrial |  |  |  |  |  |  |  |  |  |
| Institutional |  |  |  |  |  |  |  |  |  |

**GENERAL INSTRUCTIONS FOR MAKING A CODE CHANGE PROPOSAL:**

1. Check the boxes for the code or codes for which amendments are being proposed.

2. Provide the name of the local government, organization, or individual proposing the code change.

3. Proponent must sign and date the proposal as noted.

4. Provide contact information for the person designated to work with the Council and staff to supply information on the proposed changes as needed; please include name, address, phone number and e-mail address.

5. The specific section for which an amendment is proposed should be listed. The **entire section** should be reproduced, including the existing and the proposed amendatory language.

 This must be prepared in legislative style formatting. Specifically, all added words should be underlined; all deleted words should be struck through. Any separate new sections added should be inserted in the appropriate place in the existing code language in order to continue the established numbering system of the code. If more than one section is proposed for amendment or more than one page is needed for reproducing the affected section of the code, additional pages may be attached.

6. **SUPPORTING DATA REQUIREMENTS FOR ALL STATEWIDE AMENDMENT PROPOSALS:** You must attach background information with all statewide amendment proposals. The attached worksheet provides requirements for supporting data. All information will be forwarded to the Council as part of the amendment's documentation. TAG findings and projections from the worksheet will be tabulated to summarize projected benefits and impacts and will be included with TAG comments and recommendations. SBCC staff may request additional information as needed to clarify any potential impacts, and may perform additional research and analysis as needed when requested by the Council or the Workgroup on Economic Impact.

7. Please send an electronic copy of your completed proposal to SBCC staff at:

 sbcc@ga.wa.gov

**NOTE: YOU MAY REPRODUCE THIS FORM AND ADD ADDITIONAL PAGES AS NEEDED.**

1. $ / square foot of floor area or other cost. Attach data. **Construction** costs are costs prior to occupancy, and include both design and direct construction costs

 that impact the total cost of the construction to theowner/consumer. [↑](#footnote-ref-1)
2. Cost per project plan. Attach data. **Enforcement** costs include governmental review of plans, field inspection, and other action required for enforcement. [↑](#footnote-ref-2)
3. Cost/benefits to building owner/tenants over the life of the project. [↑](#footnote-ref-3)
4. Cost differential over a specific size project or range of projects as determined by the proponent. Provide sufficient cost and benefit detail to clarify the impact to the Council. All data should be created and referenced to third party reputable sources for verification. [↑](#footnote-ref-4)
5. Include measurable benefit to the user and/or public from Part II. [↑](#footnote-ref-5)