[red] indicates R1 revisions (BRFW action xx/xx/2025)

[blue] indicates R2 revisions (BRFW workshop 05/30/2025 for public review)

**Chapter 202**

**AUTOMOBILE PARKING SPACE.** A space within a *building* or private or public parking lot, exclusive of driveways, ramps, columns, office and work areas, for the parking of an automobile.

***Rationale:*** *aligns with definition in 2024 IECC Appendix RE (Electric Vehicle Charging Infrastructure).*

**AUTOMATIC LOAD MANAGEMENT SYSTEM (ALMS).**A system designed to manage electrical load across ~~one or more EV charging stations and EV Ready parking spaces~~ *EVSE spaces*.

**ELECTRIC VEHICLE (EV).** An automotive-type vehicle for on-road use, such as passenger automobiles, buses, trucks, vans, neighborhood electric vehicles and electric motorcycles, primarily powered by an electric motor that draws current from a building electrical service, *electric vehicle supply equipment* (EVSE), a rechargeable storage battery, a fuel cell, a photovoltaic array, or another source of electric current.

***Rationale:*** *aligns with definition in 2024 IECC Appendix RE (Electric Vehicle Charging Infrastructure).*

**ELECTRIC VEHICLE ~~(EV)~~ CAPABLE ~~PARKING~~ SPACE (EV CAPABLE SPACE).** A designated *automobile parking space* ~~parking space~~ that is provided with a *raceway* and electrical distribution equipment space ~~conduit, electrical panel and load capacity to support~~ *necessary for the* future installation of an *EVSE* ~~EV charging equipment~~.

***Rationale:*** *aligns with definition in 2024 IECC Appendix RE (Electric Vehicle Charging Infrastructure).*

**~~ELECTRIC VEHICLE (EV) CHARGER.~~**~~Off-board charging equipment used to charge electric vehicles.~~

***Rationale:*** *replaced by EVSE definition.*

**~~ELECTRIC VEHICLE (EV) CHARGING STATION.~~**~~EV Ready parking space with installed EV charger.~~

***Rationale:*** *replaced by EVSE space definition.*

**ELECTRIC VEHICLE ~~(EV)~~ READY ~~PARKING~~ SPACE (EV READY SPACE).**An *automobile parking space* ~~parking space~~ that is provided with ~~a receptacle outlet allowing charging of electric vehicles~~ a branch circuit and an outlet, junction box, or receptacle that will support an installed *EVSE*.

***Rationale:*** *aligns with definition in 2024 IECC Appendix RE (Electric Vehicle Charging Infrastructure).*

**ELECTRIC VEHICLE SUPPLY EQUIPMENT (EVSE).**Equipment for plug-in power transfer ~~The conductors~~, including the ungrounded, grounded, and equipment grounding conductors~~, and the~~; electric vehicle connectors~~,~~; attachment plugs~~,~~; any personal ~~personnel~~ protection system~~,~~; and all other fittings, devices, power outlets, or apparatus installed specifically for the purpose of transferring energy between the premises wiring and the ~~electric vehicle~~ *electric vehicle*.

***Rationale:*** *aligns with definition in 2024 IECC Appendix RE (Electric Vehicle Charging Infrastructure).*

**ELECTRIC VEHICLE SUPPLY EQUIPMENT INSTALLED SPACE (EVSE SPACE).** An *automobile parking space* that is provided with a dedicated *EVSE* connection.

***Rationale:*** *aligns with definition in 2024 IECC Appendix RE (Electric Vehicle Charging Infrastructure).*

**RACEWAY.** An enclosed channel of metal or nonmetallic materials designed expressly for holding wires, cables, or busbars, with additional functions as permitted in this Code.

***Rationale:*** *aligns with referenced standard 2023 NEC, Article 100.*

**Section 429—Electric vehicle charging infrastructure.**

**429.1 General.** The provisions of this section shall apply to the construction of new ~~buildings~~ *buildings* and accessory structures, including parking lots and parking garages.

~~Electric vehicle supply equipment (EVSE)~~ *Electric vehicle supply equipment (EVSE)* shall be installed in accordance with applicable requirements of chapter [**19.28**](http://app.leg.wa.gov/RCW/default.aspx?cite=19.28) RCW and the National Electrical Code, Article 625.

EXCEPTION: ~~Electric vehicle~~ *Electric vehicle* charging infrastructure is not required if any of the following conditions are met:

1. There is no public utility or commercial power supply.
2. ~~Dwelling units~~ *Buildings* and accessory structures without ~~garages or other on-site parking~~ *automobile parking spaces*.

**429.2 Electric vehicle (EV) charging infrastructure.** ~~Buildings~~ *Buildings* and accessory structures shall be provided with ~~EV charging stations~~ *EVSE spaces*, ~~EV-Ready parking spaces~~ *EV ready spaces*, and ~~EV-capable parking spaces~~ *EV capable spaces* in accordance with Table 429.2. Calculations shall be rounded up to the nearest whole number. Where a ~~building~~ *building* contains more than one occupancy, the ~~electric vehicle~~ *electric vehicle* charging infrastructure percentages of Table 429.2 shall be applied to the number of spaces required for each occupancy.

~~EXCEPTIONS: 1. Except for Group A, Group E, and Group M occupancies, on-site parking with less than 10 parking spaces shall not be required to comply with Section 429.2.~~

~~2. Group A, Group E, and Group M occupancies shall comply with one of the following, whichever is greater:~~

~~2.1. The provisions of Section 429.2 shall apply only to designated employee parking spaces.~~

~~2.2. One of each 200 parking spaces or fraction thereof shall be EV Ready. One of each 200 parking spaces or fraction thereof shall be an EV Charging Station.~~

***Question for the Council:*** *RCW 19.27.540 (2)(b) exempts “For occupancies classified as assembly, education, or mercantile, the requirements of this section apply only to employee parking spaces. The requirements of this section do not apply to occupancies classified as utility or miscellaneous.”.*

**Table 429.2**

**Electric Vehicle Charging Infrastructure**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **~~Occupancy~~ *Automobile Parking Spaces*** | | **Number of EVSE**  **~~Charging Stations~~**  **Spaces** | **Number of EV~~-~~Ready ~~Parking~~ Spaces** | **Number of EV~~-~~Capable ~~Parking~~ Spaces** |
| Group A, E, M occupancies | | | | |
| All spaces except dedicated employee spaces | | Not required | Not required | Not required |
| ~~Group A, B, E, F, H, I, M, and S occupancies~~  Dedicated employee spaces | | 10% of total ~~parking~~ spaces | 10% of total ~~parking~~ spaces | 40% ~~10%~~  of total ~~parking~~ spaces |
| Group B, F, H, I, S occupancies | | | | |
| 9 or fewer spaces | | Not required | Not required | 60% of total spaces  ~~Not required~~ |
| 10 or greater spaces | | 10% of total spaces | 10% of total spaces | 40% ~~10%~~ of total spaces |
| Group R occupancies | | | | |
|  | ~~Buildings that do not contain more than two dwelling units~~  Dedicated spaces on-site or within accessory structures for individual *dwelling units* | Not required | One for each ~~dwelling unit~~ *dwelling unit* | Not required |
|  | ~~Dwelling units with private garages~~ | ~~Not required~~ | ~~One for each dwelling unit~~ | ~~Not required~~ |
| ~~All other Group R occupancies~~  Shared spaces for multiple *dwelling units* | | 10% of total ~~parking~~ spaces | 10%~~25%~~ of total ~~parking~~ spaces | 40%~~10%~~ of total ~~parking~~ spaces |

***Question for the Council:*** *RCW 19.27.540 (2)(a) mandates “…Where parking is provided, the greater of one parking space or ten percent of parking spaces, rounded to the next whole number, must be provided with wiring or raceway sized to accommodate 208/240 V 40-amp or equivalent electric vehicle charging.”*

***Question for the Council:*** *RCW 19.27.540 (2)(b) exempts “For occupancies classified as assembly, education, or mercantile, the requirements of this section apply only to employee parking spaces. The requirements of this section do not apply to occupancies classified as utility or miscellaneous.”.*

***Question for the Council:*** *RCW 19.27.540 (3)(a) requires “all types of residential and commercial buildings to the extent necessary to support the anticipated levels of zero emissions vehicle use…”.*

**429.2.1 EVSE spaces ~~charging stations~~ and EV~~-Ready parking~~ ready spaces.** A minimum of 40-ampere dedicated 208/240-volt branch circuit shall be installed for each ~~EV Ready parking space and each EV Charging Station~~ *EVSE space* and each *EV ready space*. The branch circuits shall terminate at a receptacle outlet or ~~EV charger~~ *EVSE* in close proximity to the proposed location of the ~~EV Ready parking space or the EV Charging Station~~ *EVSE space* or *EV ready space*.

**429.2.2 EV~~-C~~capable ~~parking~~ spaces.** A listed ~~raceway~~ *raceway* capable of accommodating a minimum of 40-ampere dedicated 208/240-volt branch circuit shall be installed for each ~~EV-Capable parking space~~ *EV capable space*. A continuous ~~raceway~~ *raceway* shall be installed between an enclosure, end cap, or outlet located within close proximity of the *~~electric vehicle (EV) capable parking space~~ EV capable space* and future or existing panelboard or switchboard location(s). ~~The raceway shall terminate into a cabinet, box or other enclosure in close proximity to the proposed location of the EV-Capable parking space. Raceways~~ *Raceways* and related components that are planned to be installed underground, and in enclosed, inaccessible or concealed areas and spaces, shall be installed at the time of original construction.

**429.3 Electrical room(s) and equipment.** Electrical room(s) ~~and/~~or areas for dedicated electrical equipment shall be sized to accommodate the requirements of Section 429.2.1 through 429.2.2.

The electrical service and the electrical system, including any on-site distribution transformer(s), shall have sufficient capacity to simultaneously charge all ~~EVs~~*EVs* at all required ~~EV Charging Stations,~~ *EVSE spaces* and ~~EV Ready parking spaces~~ *EV ready spaces*~~, and EV-Capable parking spaces~~ at a minimum of 40~~-~~ amperes each.

EXCEPTION: ~~Automatic Load Management System (ALMS)~~ *Automatic Load Management System (ALMS)* may be used to adjust the maximum electrical capacity required for the ~~EV Charging stations~~ *EVSE spaces* and *EV ready spaces* ~~EV-Ready and EV-Capable parking spaces~~. The ~~ALMS~~ *ALMS* must be designed to allocate charging capacity among multiple future ~~EV Charging Stations~~ *EVSE spaces* at a minimum of 16 amperes per ~~EV charger~~ *EVSE*.

**429.4 Electric vehicle charging infrastructure for accessible parking spaces.** Ten percent of the accessible parking spaces, rounded to the next whole number, shall be ~~EV Charging Stations~~ *EVSE spaces*. An a~~A~~dditional 10 percent of the accessible parking spaces, rounded to the next whole number, shall be ~~EV Ready~~ *EV ready spaces*. Not fewer than one for each type of ~~EV charging~~ *EVSE* system shall be accessible.

The ~~electric vehicle~~ *electric vehicle* charging infrastructure may also serve adjacent parking spaces not designated as accessible parking. A maximum of 10 percent of the accessible parking spaces, rounded to the next whole number, are allowed to be included in the total number of ~~electric vehicle~~ *electric vehicle* parking spaces required under Section 429.2.

**Section 1106—Parking and passenger loading facilities.**

**1106.7 Location.** Accessible parking spaces shall be located on the shortest accessible route of travel from adjacent parking to an accessible building entrance. In parking facilities that do not serve a particular building, accessible parking spaces shall be located on the shortest route to an accessible pedestrian entrance to the parking facility. Where buildings have multiple accessible entrances with adjacent parking, accessible parking spaces shall be dispersed and located near the accessible entrances. Wherever practical, the accessible route shall not cross lanes of vehicular traffic. Where crossing traffic lanes is necessary, the route shall be designated and marked as a crosswalk.

EXCEPTION: 1. In multilevel parking structures, van accessible parking spaces are permitted on one level.

2. Accessible parking spaces shall be permitted to be located in different parking facilities if substantially equivalent or greater accessibility is provided in terms of distance from an accessible entrance or entrances, parking fee and user convenience.

This revision references the [NWPCC Power Plan](https://www.nwcouncil.org/2021powerplan_transportation-model-high-electric-case/) data to align the current and 'anticipated' levels of EV stock. With this approach, Table 429.2 has a specific reference that gets updated every 5 years to align immediate (5% current, set by statute at minimum of 10%), near-term (current code cycle = 5 year = 19.4% = 10+10%), and long-term (20 year = 57.1% = 10+10+40%).

A screenshot of a chart

AI-generated content may be incorrect.

10% EVSE-installed + 10% EV-ready = 20% also exceeds the [RCW 19.27.540](https://app.leg.wa.gov/rcw/default.aspx?cite=19.27.540) requirements for electrical room size. EV-capable parking spaces are considered in the required electrical room size, but not installed electrical service and electrical system requirements.

A screenshot of a document

AI-generated content may be incorrect.

These amendments argue a 2025 / 2030 / 2045 mix for EV / EV-ready / EV-capable of:

10% / 10% / 40% from current 10% / 25% / 10%.

The sensitivity chart below visualizes the base case vs. proposed case (EV-required vs. EV-ready vs. EV-capable). Actual costs can be applied to this simple model for first-cost comparisons.

A graph of a graph of overlay

AI-generated content may be incorrect.

For example:

EV-required = $1.00 cost (normalized)

EV-ready = $0.80, $0.60, or $0.40 cost (relative)

EV-capable = $0.00 to $0.60 cost (relative)

The intersections are the 'break even' costs to the existing base case (10/25/10). Real cost data should be requested from developers to populate the model.